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	Developer Services
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Merthyr Tydfil County Council
The Planning Division 

Unit 5 Triangle Business Park

PENTREBACH

Merthyr Tydfil

	CF48 4TQ
	Date: 27/04/2022

	
	Our Ref: PLA0065083

	
	Your Ref: P/22/0095


Dear Sir/Madam
Grid Ref: ST101996 310230 199645

Site: Taff Bargoed Centre, Trelewis, Treharris
Development: Change of use to coach parking facility with associated hardstanding area

We refer to your planning consultation relating to the above site, and we can provide the following comments in respect to the proposed development. 

Our records indicate that the proposed site is crossed by a public sewer and watermain with the approximate positions being marked on the attached Statutory Public Sewer and Water Record. Under the Water Industry Act 1991 Dwr Cymru Welsh Water has rights of access to its apparatus at all times. The required protection zone of 3 meters either side of the centre line of the sewer and 4.45 metres either side of the watermain may impact upon the proposed development and we recommend that these are given appropriate consideration during the design and determination process. 
We note from the application that the proposed development does not intend to connect to the public sewer network. Therefore, to ensure there is no detriment to the public sewerage system we request that should you be minded to grant planning permission the following Condition and Advisory Notes are included.    

Condition
SEWERAGE
No surface water and/or land drainage shall be allowed to connect directly or indirectly with the public sewerage network.

Reason: To prevent hydraulic overloading of the public sewerage system, to protect the health and safety of existing residents and ensure no pollution of or detriment to the environment.

Advisory Notes

As mentioned above the proposed development site is crossed by a public sewer and public watermain with the approximate positions being marked on the attached Statutory Public Sewer and Water Record.  The positions shall be accurately located, marked out on site before works commence and no operational development shall be carried out within a specified easement zone either side of the centreline of the public sewer or watermain. The applicant is advised to contact Welsh Water to discuss.  I enclose our Conditions for Development near Watermain(s).  It may be possible for this watermain to be diverted under Section 185 of the Water Industry Act 1991, the cost of which will be re-charged to the developer. The developer must consult Dwr Cymru Welsh Water before any development commences on site.
As of 07/01/2019, this proposed development is subject to Schedule 3 of the Flood and Water Management Act 2010. The development therefore may require approval of Sustainable Drainage Systems (SuDS) features, in accordance with the 'Statutory standards for sustainable drainage systems – designing, constructing, operating and maintaining surface water drainage systems'. It is therefore recommended that the developer engage in consultation with Merthyr Tydfil Council, as the determining SuDS Approval Body (SAB), in relation to their proposals for SuDS features. Please note, Dwr Cymru Welsh Water is a statutory consultee to the SAB application process and will provide comments to any SuDS proposals by response to SAB consultation.

The applicant may need to apply to Dwr Cymru / Welsh Water for any connection to the public sewer under S106 of the Water industry Act 1991. If the connection to the public sewer network is either via a lateral drain (i.e. a drain which extends beyond the connecting property boundary) or via a new sewer (i.e. serves more than one property), it is now a mandatory requirement to first enter into a Section 104 Adoption Agreement (Water Industry Act 1991). The design of the sewers and lateral drains must also conform to the Welsh Ministers Standards for Gravity Foul Sewers and Lateral Drains and conform with the publication "Sewers for Adoption"- 7th Edition. Further information can be obtained via the Developer Services pages of www.dwrcymru.com
The planning permission hereby granted does not extend any rights to carry out any works to the public sewerage or water supply systems without first having obtained the necessary permissions required by the Water industries Act 1991. Any alterations to existing premises resulting in the creation of additional premises or merging of existing premises must also be constructed so that each is separately connected to the Company’s water main and can be separately metered. Please contact our new connections team on 0800 917 2652 for further information on water and sewerage connections.

The applicant is also advised that some public sewers and lateral drains may not be recorded on our maps of public sewers because they were originally privately owned and were transferred into public ownership by nature of the Water Industry (Schemes for Adoption of Private Sewers) Regulations 2011. Under the Water Industry Act 1991 Dwr Cymru Welsh Water has rights of access to its apparatus at all times.

Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries, please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com
Please quote our reference number in all communications and correspondence.
Yours faithfully, 
Maria Evans
Development Control Officer

Developer Services
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Glas Cymru Cyfyngedig




Welsh Water is owned by Glas Cymru – a ‘not-for-profit’ company.

Mae Dŵr Cymru yn eiddo i Glas Cymru – cwmni ‘nid-er-elw’.
	We welcome correspondence in

Welsh and English

Dŵr Cymru Cyf, a limited company registered in

Wales no 2366777. Registered office: Pentwyn Road,

Nelson, Treharris, Mid Glamorgan CF46 6LY
	Rydym yn croesawu gohebiaeth yn y

Gymraeg neu yn Saesneg

Dŵr Cymru Cyf, cwmni cyfyngedig wedi’i gofrestru yng

Nghymru rhif 2366777. Swyddfa gofrestredig: Heol Pentwyn

Nelson, Treharris, Morgannwg Ganol CF46 6LY.
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